Request for Proposal
Wadhwani Initiative for Sustainable Health Care (WISH) is the flagship program of Lords Education & Health Society (LEHS), a society registered under Society Registration Act, 1862. LEHS works towards improving the quality of life and access to primary healthcare services for the underserved communities. The Organization is implementing primary healthcare models through partnership with state governments, international agencies and the private sector by appropriately introducing promising healthcare innovations in the public health system in order to build an equitable, innovation-led and evidence-based quality healthcare system within easy reach of the underserved population of Rajasthan, Madhya Pradesh, Delhi, Uttar Pradesh and Assam. 
LEHS invites proposals (technical & financial) from authorized brand partners for installation, testing & commissioning of following equipment’s:
Site Location: AIIMS BIBINAGAR Telangana 
A) Online UPS with the given below specifications:
	ONLINE UPS
	100KVA Double Conversion Online UPS System 3 phase input - 3phase output

	Batteries
	Sealed Maintenance free batteries ~30 - 40 minutes battery backup on 0.8 p.f Load.

	Accessories
	UPS Accessories like, Battery rack, Battery Breaker with enclosure, Battery interlinks, BCB cables, lugs, DC cables, Network Card, Cable for UPS to Battery Bank up to 15 meters etc

	Service Charges
	Installation, Testing & Commissioning Charges


Preferred Brand: Emerson/Schneider Electric however quality products from other brands are welcome
B) 100% Fresh Air Double Skin Floor Mounted AHU with the given below specifications:
	S.NO
	DESCRIPTION OF ITEM
	UNIT
	QTY

	1
	IEC UNIT 
	 
	 

	1.1
	Supplying, installing, testing and commissioning of DOUBLE Skin Floor mounted AHU, consisting of Mixing bxo, 20mic,10 Mic, Cooling coil, Fan,5 mic, hepa 0.3 mic Filter sections only. Frame : Aluminium Extruded Anodized Penta post frame with polyamide corners Panels : Outer 24 G GI Pre- coated sheet Panels : Inner 24 g GI plain sheet Insulation : 25 mm tk. PUF, density 42 kg/m3 Fan: Imported Nicotra/Kruger, DIDW, backward Curved Blower Drive : Belt, with Taper lock pulleys Motor : NON Flame proof Foot Mounted Induction -4pole 3PH, EFF1/IE2 make : KE/CG/BB/ Cooling Coil: Aluminium finned copper tube DX coil, 1/2" pipe dia - with MS 'B' CLASS Header's Drain SS 304 G - 22G drain pain with Foam insulation Pre Filters :20 mic Flange type- 50 mm tk., with filters Pre Filters :10 mic Flange type- 150 mm tk., with filters fine Filters :5 mic Flange type- 300 mm tk., with filters HEPA Filters :0.3 mic Flange type- 300 mm tk., with filters Accessories: UV LAMP and View Glass
	 
	 

	 
	Capacity: 17600 CFM, 
	1.00
	Nos

	1.2
	Supplying, installing, testing and commissioning of indoor electrical panel set
	 
	 

	 
	Capacity: 11 TR / 4400 CFM 
	4.00
	Nos

	1.3
	Supply and Installation of 11 TR DX Air cooled condensing unit suitable for R 410 C refrigerant Gas and comprises of Fixed Scroll compressor and the air-Cooled condenser fan with Condenser coil 
	 
	 

	 
	CARRIER MAKE DX TYPE CONDENSOR UNIT 11 TR WITH 410 REFRIGERANT
	4.00
	No

	1.4
	 Supplying, installing, testing and commissioning of DOUBLE Skin Floor mounted Exhaust AHU,  Frame : Aluminium Extruded Anodized penta post frame with polyamide corners Panels : Outer 24 G GI Pre- coated sheet Panels : Inner 24 g GI plain sheet Insulation : 25 mm tk. PUF, density 42 kg/m3 Fan: Imported Nicotra/Kruger, DIDW, backward Curved Blower Drive : Belt, with Taper lock pulleys Motor : NON Flame proof Foot Mounted Induction -4pole 3PH, EFF1/IE2 make : KE/CG/BB/   with filters Pre Filters :10 mic Flange type- 150 mm tk., with filters fine Filters :5 mic Flange type- 300 mm tk., with filters HEPA Filters :0.3 mic Flange type- 300 mm tk., with filters Accessories: UV LAMP .
	 
	 

	 
	Capacity: 8000 CFM 
	2.00
	Nos

	1.5
	Supply of ERC along with Expansion valves and on/ off valves and driers for above Units
	4.00
	Sets

	2
	SITC of factory fabricated GSS Ducting (with minimum 120 Gsm) as per SMACNA/IS standards with splitters, bends, elbows, vanes, stiffening supports, gasket, nuts, bolts, TDF flanges, GI full threaded rods and slotted rail/ MS supports, raiser duct supports as scheduled as per the specifications and approved drawings.
	 
	 

	 
	24 Gauge (0- 750 mm) - 0.63 mm Thk
	75
	Sq.m

	 
	22 Gauge (751 - 1500 mm) - 0.8 mm Thk
	110
	Sq.m

	 
	Supplying & fixing of powder coated ms fabricated L angle to run duct outside 
	30
	nos

	3
	SITC of supply / return air Grille constructed with powder coated aluminium extruded section, grill frame shall have 1.5mm thick & 30mm flange width, louver shall be of 5mm thickness with 0 / 15 Deg Deflection, installed with necessary screws & accessories. Grill shall be of removable core type
	8
	Sq.m

	 
	SITC of Collar Damper made of Aluminium Extruded section with frame of 1mm thick, key operated type, with black anodised Finish, installed along with necessary support & accessories.
	5
	sqm

	4
	 
	 
	 

	 
	SITC of Acoustic Insulation made of Open Cell elastomeric Nitrile rubber insulation, Class 1 fire performance conforming to BS 475 Part 7, with thermal conductivity of 0.047 W/m.K, density 140 to 180 Kg/ Cu.m, The insulation manufactured as per BS 476 Part 7 & meets UL 94test  supplementary materials for air distribution system  and does not absorbs less 0.2% water by volume (ASTM c 209), does not support microbial growth does not emit objectionable odors (ASTM C 665) and has thermal conductivity of 0.04W/m K @ 20 degC . and water vapor permeance of 0.10. Adhesive used additionally with VOC level not exceeding 50 grms / Litre. 
	 
	 

	 
	15 mm THK
	50
	Sq.m

	5
	 
	 
	 

	 
	SITC of Thermal Insulation of closed cell, Nitrile rubber insulation for ducts, Class O Fire propagation tested according to BS 476, FM approved, with thermal conductivity 0.035 W/m. K @ 0 deg C, density 40 to 60 Kg/ Cu.m. The insulation manufactured as per BS 476 Part 7test & which meets UL94 supplementary materials for air distribution system which does not absorb less 0.2% water by volume (ASTM D 1056), does not support microbial growth (ASTM D2180, G21, G22) and does not emit objectionable odours (ASTM C 665) and has thermal conductivity of 0.033W/m.k @ 0deg C as per DIN EN 12667. and water vapor permeance of 0.10.   Joints shall be sealed with 50 mm wide 3 mm thick self-adhesive tape. Adhesive shall be used additionally with VOC level not exceeding 50 grams / Litre.
	 
	 

	 
	13 mm THK
	200
	Sq.m

	6
	SITC of Volume Control dampers made of GI Frame of 18G & Blade of 20G, opossed blade type, blade spindle connected with self-lubricated bronze bush, damper is operated by means of lever & falt linkage connected to the spindle, vcd installed on duct along with necessary support & accessories
	6
	Sq.m

	7
	SITC of Fresh air & Exhaust air louvers of powder coated extruded aluminium construction with all side flanges having 1.2mm thickness and louver of 1mm thick, installed with integral insect screen & proper support & accessories
	1.00
	set

	8
	SITC of 18 SWG Hard drawn Copper Refrigerant Piping for Ductable & condensing units of the following sizes including 19 mm thick nitrile tube insulation including mechanical protection with 7 mil Glass Woven glass cloth of various sizes, supports with required hardware etc. (The piping shall be neatly done ladder type GI tray support with proper PVC saddles.), necessary copper fittings & accessories shall be considered while costing.  All exposed piping insulation shall have a UV protection and proper cover 
	 
	 

	 
	5/8" (15.9mm) dia
	80
	Rmt

	 
	1 1/8" (28.6mm) dia
	80
	Rmt

	9
	Supply, laying, testing & commissioning of FRLS copper flexible control cable installed in 19mm PVC conduit along with necessary support and accessories. 
	 
	 

	 
	3C x 2.5Sq.mm for power supply 
	120.00
	Rmt

	 
	4C x 1.5Sq.mm for communication
	120.00
	Rmt

	10
	SITC of Rigid PVC (4 KG duty) drain pipe complete with all fittings like couplers, elbows, tees etc with 6 MM Nitrile Rubber insulation, installed with required wall chasing, supports & clamps, etc. The necessary solvent/adhesive is included in the scope of work to join the pipe & fittings.
	 
	 

	 
	32 mm (DIA)
	20.00
	Rmt

	11
	MS stands for ODUs 
	4.00
	Sets

	12
	Testing / commissioning of the above systems
	1.00
	Sets


Mandatory requirements for both A & B items:
	1
	Minimum 3 years replacement warranty

	2
	3 Year insurance coverage for any type of damages not covered in warranty

	3
	10% retention to be released within 30 days after successful handover

	4
	All equipment shall be installed, operated, demonstrated and handed over with in the time line mentioned in RFP

	5
	Cost of extended warranty to be mentioned separately

	6
	Cost of Insurance to be mentioned separately


Preferred Brand: Brands having UKAS/ISO/BIS will be preferred
Please refer the below instructions before submitting your proposals:
· Technical and Financial proposals should be shared in PDF & Excel respectively on the designated email id only.
· The above should be in one email and not to be shared in two separate emails.
· Pls mention the JOB ID XXXX in the subject line while sharing your proposals (pls refer the Devnet advertisement for JOB ID).
· Kindly mention your payment & delivery terms in the bid.
· Taxes should be mentioned separately and clearly.
· The quantities mentioned are tentative and may change at the time of placing the order.

· LEHS reserves the right to award the contract to one or more bidders, accordingly the final quantities required may be divided among successful bidders. The quantities so divided will be at sole discretion of LEHS.

· LEHS reserves the right to cancel the bid(s) and may call for fresh bids. LEHS also has the right to reject any bid without assigning any reason.

· If there is delay in delivery, the penalty clause will be imposed as per LEHS policy. LEHS also reserves the right to cancel the entire order in case of delay for more than 10 days from the scheduled delivery dates.

· Bids incomplete in any respect, will not be considered for evaluation.
· LEHS is not liable to pay anything towards preparation of proposal or site visit.
Mandatory Documents to be submitted with proposal:

Please submit the following as enclosures or attachment with your proposal. 

· Copy of registration documents/certificate and most recent renewal as a legal entity.

· License or permission, if any for doing business. 

· Copy of Authorized dealership issued by the company if any.

· PAN Copy

· GST Registration copy 
· Copy of latest 5 PO’s for the similar work
Interested vendors are requested to submit detailed proposals along with the payment plan by e-mail only at  rfp@wishfoundationindia.org latest by 5 pm, 15 June, 2021 and address to: The Chief Executive Officer, Lords Education & Health Society. The proposals received after the due date will not be considered.

